## Sheet1
Stream No. |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
Description |  | Two Phase from Interface to HP Separator | HP Steam to Scrubbing Line | HP Steam Scrubbing Spray Water Supply | HP Steam Scrubbing Line | HP Steam Condensate Pots | HP Scrubber Condensate | HP Steam to Power Plant Bifurcation | Ejector Steam | HP Steam to Turbine Strainer 1 | HP Steam to Turbine Strainer 2 | HP Brine to LP Separator Control Valve | LP Steam to LP Scrubbing Line | LP Steam Scrubbing Spray Water Supply | LP Steam Scrubbing Line | LP Steam Condensate Pots | LP Demister Condensate | LP Steam to Power Plant Bifurcation | LP Steam to Turbine Strainer 1 | LP Steam to Turbine Strainer 2 | LP Brine to Reinjection Pumps | LP Brine Reinjection Pumps Discharge
Pipe True Length (m) |  | 49 | 7 | 150 | 160 | N/A | N/A | 90 | 10 | 4 | 24 | 55 | 12 | 150 | 93 | N/A | N/A | 76 | 4 | 20 | 73.45 | TBA
Nominal Pipe Diameter (mm) |  | 1050 | 1200 | 80 | 1200 | 750 | 100 | 1200 | 250 | 750 | 750 | 750 | 1200 | 80 | 1200 | 750 | 100 | 1200 | 900 | 900 | 600 | 600
Flow (t/h) | Steam | 472.4731 | 474.7957 | - | 472.8003 | - | - | 472.8003 | 22.2216 | 225.2893 | 225.2893 | - | 176.8133 | - | 176.2933 | - | - | 176.2936 | 88.1468 | 88.1468 | - | -
| Liq. Water | 1387.6688 | 0.69267 | 9.7179 | 12.406 | 7.1669 | 5.238 | 0.0010478 | 4.9247e-05 | 0.00049928 | 0.00049928 | 1384.6536 | 0.51469 | 3.5466 | 4.5813 | 2.8949 | 1.6861 | 4.8519e-06 | 2.426e-06 | 2.426e-06 | 1207.3256 | 1207.3256
| Impurities | 3.7581 | 0.001879 | - | 0.001879 | 0.0010855 | 0.00079352 | 1.587e-07 | 1.587e-07 | 7.4591e-09 | 7.5623e-08 | 7.5623e-08 | 0.00093906 | 0.0018781 | - | 0.0018781 | 0.00069134 | 0.0006912 | 1.3827e-07 | 1.3827e-07 | 6.9134e-08 | 6.9134e-08
| NCG | 11.1 | 11.1 | - | 11.1 | - | - | 11.1 | 0.5217 | 5.2892 | 5.2892 | - | - | - | - | - | - | - | - | - | - | -
| Total | 1875 | 486.5902 | 9.7179 | 496.3081 | 7.168 | 5.2388 | 483.9013 | 22.7434 | 230.579 | 230.579 | 1384.6536 | 177.3289 | 3.5485 | 180.8746 | 2.8968 | 1.6868 | 176.2943 | 88.1468 | 88.1468 | 1207.3256 | 1207.3256
Upstream Pressure (bara) |  | 11.9991 | 11.6168 | TBA | 11.6095 | N/A | 11.5427 | 11.3975 | 11.3014 | 11.3014 | 11.2987 | 11.6168 | 2.0503 | TBA | 2.0377 | N/A | 2.0086 | 1.8943 | 1.8136 | 1.8116 | 2.0503 | TBA
Downstream Pressure (bara) |  | 11.8168 | 11.6095 | TBA | 11.5545 | N/A | 11.4175 | 11.3014 | 11.2894 | 11.278 | 11.278 | 11.6657 | 2.0377 | TBA | 2.0168 | N/A | 1.9087 | 1.8136 | 1.805 | 1.805 | 2.4567 | 11
Temperature (°C) |  | 187.1812 | 186.058 | 37.6 | 185.9359 | 185.9359 | 185.5404 | 185.0302 | 184.8177 | 184.7951 | 184.7898 | 186.4557 | 120.9011 | 37.6 | 120.6401 | 120.6401 | 119.5522 | 118.9856 | 118.4787 | 118.4732 | 120.9011 | 120.9011
Superheat (ºC) |  | N/A | 0 | N/A | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | N/A | 0.62748 | 1.1549 | 1.4061 | 1.4184
Upstream Enthalpy (kJ/kg) |  | 1300 | 2779.691 | 157.5111 | 2731.2277 | 789.4791 | 2758.7848 | 2780.2846 | 2779.7879 | 2779.7879 | 2779.7879 | 791.7905 | 2700.8558 | 157.5111 | 2651.1301 | 506.5058 | 2685.2865 | 2705.2591 | 2704.6797 | 2704.6797 | 511.2881 | 511.2881
Downstream Enthalpy (kJ/kg) |  | 1299.9364 | 2779.6522 | 157.5111 | 2730.3598 | N/A | 2758.632 | 2780.2846 | 2779.7879 | 2779.393 | 2779.7564 | 2779.5989 | 2700.8558 | 2700.7626 | 157.5111 | 2650.4246 | 2685.2865 | N/A | 2705.2591 | 2704.6797 | 2704.632 | 2704.4411
Average Steam Quality |  | 0.254 | 0.99854 | 0 | 0.97443 | 0 | 0.98843 | 0.99942 | 0.99925 | 0.99926 | 0.99927 | 0 | 0.9971 | 0 | 0.97467 | 0 | 0.99092 | 1 | 1 | 1 | 0 | 0
Superficial Steam Velocity (m/s) |  | 25.8697 | 20.8345 | - | 20.7917 | N/A | - | 21.1994 | 22.8735 | 26.2362 | 26.2392 | - | 38.7018 | - | 38.8864 | N/A | - | 42.2789 | 38.4091 | 38.4297 | - | TBA
Average Fluid Velocity (m/s) |  | 26.3904 | 20.8347 | 0.88323 | 20.7953 | N/A | 0.2531 | 21.1995 | 22.8736 | 26.2363 | 26.2394 | 1.0456 | 38.6824 | 0.30899 | 38.8876 | N/A | - | 42.2789 | 38.4091 | 38.4297 | 1.3614 | TBA